|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Extinguisher****Type** | **Inspection****(7.2.1.2)** | **Maintenance****(7.3.2)** | **Internal Examination****(7.3.3.1)** | **Hydrostatic****Testing****(8.3.1)** |
| **Dry Chemical****(Stored Pressure)** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |
| **Carbon Dioxide** | Once per calendar month, not to exceed 31 days | Maintenance &conductivitytest at 1 year | 5 years | 5 years |
| **Water (Stored****Pressure)** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **Dry Chemical****(Stainless Steel)** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **Dry Chemical****(Cartridge)** | Once per calendar month, not to exceed 31 days | 1 year | 1 year | 12 years |
| **Wet Chemical** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **AFFF (Liquid****Charge Type)** | Once per calendar month, not to exceed 31 days | 1 year | 3 years | 5 years |
| **FFFP (Liquid****Charge Type)** | Once per calendar month, not to exceed 31 days | 1 year | 3 years | 5 years |
| **Dry Powder** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |
| **Dry Powder****(Cartridge)** | Once per calendar month, not to exceed 31 days | 1 year | 1 year | 12 years |
| **Halogenated****Agents** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |

 **\*Per NFPA 10, 2013 edition.**