|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Extinguisher**  **Type** | **Inspection**  **(7.2.1.2)** | **Maintenance**  **(7.3.2)** | **Internal Examination**  **(7.3.3.1)** | **Hydrostatic**  **Testing**  **(8.3.1)** |
| **Dry Chemical**  **(Stored Pressure)** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |
| **Carbon Dioxide** | Once per calendar month, not to exceed 31 days | Maintenance &  conductivity  test at 1 year | 5 years | 5 years |
| **Water (Stored**  **Pressure)** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **Dry Chemical**  **(Stainless Steel)** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **Dry Chemical**  **(Cartridge)** | Once per calendar month, not to exceed 31 days | 1 year | 1 year | 12 years |
| **Wet Chemical** | Once per calendar month, not to exceed 31 days | 1 year | 5 years | 5 years |
| **AFFF (Liquid**  **Charge Type)** | Once per calendar month, not to exceed 31 days | 1 year | 3 years | 5 years |
| **FFFP (Liquid**  **Charge Type)** | Once per calendar month, not to exceed 31 days | 1 year | 3 years | 5 years |
| **Dry Powder** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |
| **Dry Powder**  **(Cartridge)** | Once per calendar month, not to exceed 31 days | 1 year | 1 year | 12 years |
| **Halogenated**  **Agents** | Once per calendar month, not to exceed 31 days | 1 year | 6 years | 12 years |

**\*Per NFPA 10, 2013 edition.**